## CABLES
CABLE | DESCRIPTION | LOAD_TYPE | LOAD_KW | SEG1 | SEG2 | SEG3 | SEG4 | SEG5 | SEG6 | SEG7 | SEG8 | SEG9 | SEG10 | SEG11 | SEG12 | SEG13 | SEG14 | SEG15 | SEG16 | SEG17 | SEG18 | SEG19 | SEG20 | SEG21 | SEG22 | SEG23 | SEG24 | SEG25 | SEG26 | SEG27 | SEG28 | SEG29 | SEG30 | SEG31 | SEG32 | SEG33 | SEG34 | SEG35 | SEG36 | SEG37 | SEG38 | SEG39 | SEG40 | SEG41 | SEG42 | SEG43 | SEG44 | SEG45 | SEG46 | SEG47 | SEG48 | SEG49 | SEG50 | SEG51 | SEG52 | SEG53 | SEG54 | SEG55 | SEG56 | SEG57 | SEG58 | SEG59 | SEG60 | SEGL1 | SEGL2 | SEGL3 | SEGL4 | SEGL5 | SEGL6 | SEGL7 | SEGL8 | SEGL9 | SEGL10 | SEGL11 | SEGL12 | SEGL13 | SEGL14 | SEGL15 | SEGL16 | SEGL17 | SEGL18 | SEGL19 | SEGL20 | SEGL21 | SEGL22 | SEGL23 | SEGL24 | SEGL25 | SEGL26 | SEGL27 | SEGL28 | SEGL29 | SEGL30 | SEGL31 | SEGL32 | SEGL33 | SEGL34 | SEGL35 | SEGL36 | SEGL37 | SEGL38 | SEGL39 | SEGL40 | SEGL41 | SEGL42 | SEGL43 | SEGL44 | SEGL45 | SEGL46 | SEGL47 | SEGL48 | SEGL49 | SEGL50 | SEGL51 | SEGL52 | SEGL53 | SEGL54 | SEGL55 | SEGL56 | SEGL57 | SEGL58 | SEGL59 | SEGL60 | SEGL_TOTAL | FITOFF | XCAPACITY | ESTIMATED_CABLE_LENGTH | SEGD1 | SEGD2 | SEGD3 | SEGD4 | SEGD5 | SEGD6 | SEGD7 | SEGD8 | SEGD9 | SEGD10 | SEGD11 | SEGD12 | SEGD13 | SEGD14 | SEGD15 | SEGD16 | SEGD17 | SEGD18 | SEGD19 | SEGD20 | SEGD21 | SEGD22 | SEGD23 | SEGD24 | SEGD25 | SEGD26 | SEGD27 | SEGD28 | SEGD29 | SEGD30 | SEGD31 | SEGD32 | SEGD33 | SEGD34 | SEGD35 | SEGD36 | SEGD37 | SEGD38 | SEGD39 | SEGD40 | SEGD41 | SEGD42 | SEGD43 | SEGD44 | SEGD45 | SEGD46 | SEGD47 | SEGD48 | SEGD49 | SEGD50 | SEGD51 | SEGD52 | SEGD53 | SEGD54 | SEGD55 | SEGD56 | SEGD57 | SEGD58 | SEGD59 | SEGD60 | SEGM1 | SEGM2 | SEGM3 | SEGM4 | SEGM5 | SEGM6 | SEGM7 | SEGM8 | SEGM9 | SEGM10 | SEGM11 | SEGM12 | SEGM13 | SEGM14 | SEGM15 | SEGM16 | SEGM17 | SEGM18 | SEGM19 | SEGM20 | SEGM21 | SEGM22 | SEGM23 | SEGM24 | SEGM25 | SEGM26 | SEGM27 | SEGM28 | SEGM29 | SEGM30 | SEGM31 | SEGM32 | SEGM33 | SEGM34 | SEGM35 | SEGM36 | SEGM37 | SEGM38 | SEGM39 | SEGM40 | SEGM41 | SEGM42 | SEGM43 | SEGM44 | SEGM45 | SEGM46 | SEGM47 | SEGM48 | SEGM49 | SEGM50 | SEGM51 | SEGM52 | SEGM53 | SEGM54 | SEGM55 | SEGM56 | SEGM57 | SEGM58 | SEGM59 | SEGM60 | CALCULATED_AMPS | AMBIENT | AMBIENT_DERATING | AMP_RATING | INSTALL_METHOD | CABLESIZE_METHOD1 | MAX_VDROP | VC_CALC | CABLESIZE_METHOD2 | INITIAL_CABLESIZE | OVERRIDE_CABLESIZE | SELECTED_CABLESIZE | RECOMMEND_PDEVICE | OVERRIDE_PDEVICE | SELECTED_PDEVICE | PDEVICE_CURVE | PDEVICE_IA | CONDUCTOR_MATERIAL | MATERIAL_CONSTANT | SPH | SPE | LMAX | LMAX SATISFIED | CABLE_DIAMETER | CABLE_MASS | LOAD_AMPS | CABLE_SIZE | CABLE_LENGTH | PROTECTION_DEVICE
M01PU1121 | LOADIN 1 SILOS PUMP 1 | VSD | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 5 | 1.2 | 62.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5 | 0 | 16.5 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0 | 0.41 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.0563 | 45 | 0.94 | 25.6 | UNENCLOSED_TOUCHING | 4 | 28 | 17.528 | 2.5 | 4 |  | 4 | 25 |  | 25 | C | 162.5 | COPPER | 0.0225 | 4 | 2.5 | 77.4227 | PASS | 16.5 | 0.41 | 24.1 | 4 | 62.4 | 25
M02PU1121 | LOADIN 2 SILOS PUMP 1 | VSD | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 22 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 5 | 1.2 | 82.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.4 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.4 | 0 | 17.4 | 17.4 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0 | 0.49 | 0.49 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.0563 | 45 | 0.94 | 25.6 | UNENCLOSED_TOUCHING | 4 | 28 | 13.2095 | 4 | 4 | 6 | 6 | 25 |  | 25 | C | 162.5 | COPPER | 0.0225 | 6 | 2.5 | 88.8084 | PASS | 17.4 | 0.49 | 24.1 | 6 | 82.8 | 25
M02PU1122 | LOADIN 2 SILOS PUMP 2 | VSD | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 22 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 5 | 1.2 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4 | 0 | 18.4 | 18.4 | 18.4 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62 | 0.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62 | 0 | 0.62 | 0.62 | 0.62 | 0.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.0563 | 45 | 0.94 | 25.6 | UNENCLOSED_TOUCHING | 4 | 28 | 11.9929 | 4 | 4 | 10 | 10 | 25 |  | 25 | C | 162.5 | COPPER | 0.0225 | 10 | 4 | 143.7851 | PASS | 18.4 | 0.62 | 24.1 | 10 | 91.2 | 25
M03PU2011 | RM SILOS TO SEP 1 PUMP | DOL | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 5 | 1.2 | 63.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 46.8353 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 12 | 0.21 | 8.9 | 2.5 | 63.6 | 10
M03PU2012 | RM SILOS TO SEP 2 PUMP | DOL | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 5 | 1.2 | 63.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 46.8353 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 12 | 0.21 | 8.9 | 2.5 | 63.6 | 10
M03PU2097 | RM SILOS CIPR PUMP | DOL | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 5 | 1.2 | 63.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6413 | 45 | 0.94 | 18.8 | UNENCLOSED_TOUCHING | 2.5 | 28 | 23.4176 | 2.5 | 2.5 |  | 2.5 | 20 |  | 20 | C | 130 | COPPER | 0.0225 | 2.5 | 2.5 | 78.6325 | PASS | 12 | 0.21 | 17.7 | 2.5 | 63.6 | 20
M03AG2102 | RM SILO 1 AGITATOR | DOL | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 5 | 1.2 | 63.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4056 | 45 | 0.94 | 2.6 | UNENCLOSED_TOUCHING | 1 | 28 | 169.3275 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 2.5 | 2.5 | 63.6 | 6
M03AG2202 | RM SILO 2 AGITATOR | DOL | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 5 | 1.2 | 63.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4056 | 45 | 0.94 | 2.6 | UNENCLOSED_TOUCHING | 1 | 28 | 169.3275 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 2.5 | 2.5 | 63.6 | 6
M03AG2302 | RM SILO 3 AGITATOR | DOL | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 5 | 1.2 | 63.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4056 | 45 | 0.94 | 2.6 | UNENCLOSED_TOUCHING | 1 | 28 | 169.3275 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 2.5 | 2.5 | 63.6 | 6
M15PU3110 | SEP 1 FEED PUMP | VSD | 7.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 5 | 1.2 | 43.2 | 14.5 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.0281 | 45 | 0.94 | 12.8 | UNENCLOSED_TOUCHING | 1.5 | 28 | 50.6366 | 2.5 | 2.5 |  | 2.5 | 16 |  | 16 | C | 104 | COPPER | 0.0225 | 2.5 | 2.5 | 98.2906 | PASS | 14.5 | 0.33 | 12.1 | 2.5 | 43.2 | 16
M15CC3120 | SEP 1 SEPARATOR | VSD | 45 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 5 | 1.2 | 48 | 25.6 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.6 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.62 | 1.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.62 | 1.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.1688 | 45 | 0.94 | 76.8 | UNENCLOSED_TOUCHING | 25 | 28 | 7.5955 | 6 | 25 | 35 | 35 | 80 |  | 80 | C | 520 | COPPER | 0.0225 | 35 | 10 | 122.3172 | PASS | 25.6 | 1.62 | 72.2 | 35 | 48 | 80
M15PU3150 | SEP 1 CREAM PUMP | VSD | 1.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 5 | 1.2 | 43.2 | 14.5 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4056 | 45 | 0.94 | 2.6 | UNENCLOSED_TOUCHING | 1 | 28 | 249.2877 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 2.5 | 2.5 | 43.2 | 6
M15PU3158 | LP SKIM 1 TRANSFER PUMP | DOL | 11 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 5 | 1.2 | 48 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6413 | 45 | 0.94 | 18.8 | UNENCLOSED_TOUCHING | 2.5 | 28 | 31.0284 | 2.5 | 2.5 |  | 2.5 | 20 |  | 20 | C | 130 | COPPER | 0.0225 | 2.5 | 2.5 | 78.6325 | PASS | 12 | 0.21 | 17.7 | 2.5 | 48 | 20
M15PU3160 | SEP 1 CREAM PHE CHW PUMP | DOL | 2.2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 5 | 1.2 | 43.2 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5283 | 45 | 0.94 | 3.8 | UNENCLOSED_TOUCHING | 1 | 28 | 170.5653 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 3.6 | 2.5 | 43.2 | 6
M15PU3180 | SEP 1 PHE HW PUMP | DOL | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 5 | 1.2 | 43.2 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.415 | 45 | 0.94 | 6.9 | UNENCLOSED_TOUCHING | 1 | 28 | 93.9345 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 12 | 0.21 | 6.5 | 2.5 | 43.2 | 10
M16PU3110 | SEP 2 FEED PUMP | VSD | 7.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 5 | 1.2 | 43.2 | 14.5 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.0281 | 45 | 0.94 | 12.8 | UNENCLOSED_TOUCHING | 1.5 | 28 | 50.6366 | 2.5 | 2.5 |  | 2.5 | 16 |  | 16 | C | 104 | COPPER | 0.0225 | 2.5 | 2.5 | 98.2906 | PASS | 14.5 | 0.33 | 12.1 | 2.5 | 43.2 | 16
M16CC3120 | SEP 2 SEPARATOR | VSD | 45 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 5 | 1.2 | 48 | 22.8 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | 1.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | 1.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.1688 | 45 | 0.94 | 76.8 | UNENCLOSED_TOUCHING | 25 | 28 | 7.5955 | 6 | 25 |  | 25 | 80 |  | 80 | C | 520 | COPPER | 0.0225 | 25 | 6 | 76.0959 | PASS | 22.8 | 1.22 | 72.2 | 25 | 48 | 80
M16PU3150 | SEP 2 CREAM PUMP | VSD | 1.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 5 | 1.2 | 43.2 | 14.5 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4056 | 45 | 0.94 | 2.6 | UNENCLOSED_TOUCHING | 1 | 28 | 249.2877 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 2.5 | 2.5 | 43.2 | 6
M16PU3158 | LP SKIM 2 TRANSFER PUMP | DOL | 11 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 5 | 1.2 | 48 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6413 | 45 | 0.94 | 18.8 | UNENCLOSED_TOUCHING | 2.5 | 28 | 31.0284 | 2.5 | 2.5 |  | 2.5 | 20 |  | 20 | C | 130 | COPPER | 0.0225 | 2.5 | 2.5 | 78.6325 | PASS | 12 | 0.21 | 17.7 | 2.5 | 48 | 20
M16PU3160 | SEP 2 CREAM PHE CHW PUMP | DOL | 2.2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 5 | 1.2 | 43.2 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5283 | 45 | 0.94 | 3.8 | UNENCLOSED_TOUCHING | 1 | 28 | 170.5653 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 3.6 | 2.5 | 43.2 | 6
M16PU3180 | SEP 2 PHE HW PUMP | DOL | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 5 | 1.2 | 43.2 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.415 | 45 | 0.94 | 6.9 | UNENCLOSED_TOUCHING | 1 | 28 | 93.9345 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 12 | 0.21 | 6.5 | 2.5 | 43.2 | 10
M05PU1027 | UF1 PLANT FEED PUMP | VSD | 11 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 5 | 1.2 | 50.4 | 14.5 | 14.5 | 0 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6413 | 45 | 0.94 | 18.8 | UNENCLOSED_TOUCHING | 2.5 | 28 | 29.5508 | 2.5 | 2.5 |  | 2.5 | 20 |  | 20 | C | 130 | COPPER | 0.0225 | 2.5 | 2.5 | 78.6325 | PASS | 14.5 | 0.33 | 17.7 | 2.5 | 50.4 | 20
M05PU1038 | UF1 PLANT RET PUMP | VSD | 3 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 5 | 1.2 | 50.4 | 14.5 | 14.5 | 0 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8113 | 45 | 0.94 | 5.2 | UNENCLOSED_TOUCHING | 1 | 28 | 106.8376 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 4.9 | 2.5 | 50.4 | 6
M05PU1050 | UF1 PLANT PERM PUMP | VSD | 5.5 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 5 | 1.2 | 50.4 | 14.5 | 14.5 | 0 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 59.1017 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 14.5 | 0.33 | 8.9 | 2.5 | 50.4 | 10
M05PU1060 | UF1 PLANT PERM PHE HW PUMP | DOL | 3 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 5 | 1.2 | 50.4 | 12 | 12 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8113 | 45 | 0.94 | 5.2 | UNENCLOSED_TOUCHING | 1 | 28 | 106.8376 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 4.9 | 2.5 | 50.4 | 6
M05PU1093 | UF1 PLANT CIP BOOST PUMP | VSD | 11 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 5 | 1.2 | 50.4 | 14.5 | 14.5 | 0 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6413 | 45 | 0.94 | 18.8 | UNENCLOSED_TOUCHING | 2.5 | 28 | 29.5508 | 2.5 | 2.5 |  | 2.5 | 20 |  | 20 | C | 130 | COPPER | 0.0225 | 2.5 | 2.5 | 78.6325 | PASS | 14.5 | 0.33 | 17.7 | 2.5 | 50.4 | 20
M05PU1100 | UF1 PLANT LOOP 1 PUMP | VSD | 30 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 8 | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 5 | 1.2 | 62.4 | 20.3 | 20.3 | 0 | 20.3 | 20.3 | 20.3 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86 | 0.86 | 0 | 0.86 | 0.86 | 0.86 | 0.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.1125 | 45 | 0.94 | 51.2 | UNENCLOSED_TOUCHING | 16 | 28 | 8.764 | 6 | 16 |  | 16 | 50 |  | 50 | C | 325 | COPPER | 0.0225 | 16 | 6 | 109.7995 | PASS | 20.3 | 0.86 | 48.2 | 16 | 62.4 | 50
M05PU1200 | UF1 PLANT LOOP 2 PUMP | VSD | 30 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 8 | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 5 | 1.2 | 62.4 | 20.3 | 20.3 | 0 | 20.3 | 20.3 | 20.3 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86 | 0.86 | 0 | 0.86 | 0.86 | 0.86 | 0.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.1125 | 45 | 0.94 | 51.2 | UNENCLOSED_TOUCHING | 16 | 28 | 8.764 | 6 | 16 |  | 16 | 50 |  | 50 | C | 325 | COPPER | 0.0225 | 16 | 6 | 109.7995 | PASS | 20.3 | 0.86 | 48.2 | 16 | 62.4 | 50
M06PU1027 | UF2 PLANT FEED PUMP | VSD | 11 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 5 | 1.2 | 61.2 | 14.5 | 14.5 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6413 | 45 | 0.94 | 18.8 | UNENCLOSED_TOUCHING | 2.5 | 28 | 24.336 | 2.5 | 2.5 |  | 2.5 | 20 |  | 20 | C | 130 | COPPER | 0.0225 | 2.5 | 2.5 | 78.6325 | PASS | 14.5 | 0.33 | 17.7 | 2.5 | 61.2 | 20
M06PU1038 | UF2 PLANT RET PUMP | VSD | 3 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 5 | 1.2 | 61.2 | 14.5 | 14.5 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8113 | 45 | 0.94 | 5.2 | UNENCLOSED_TOUCHING | 1 | 28 | 87.9839 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 4.9 | 2.5 | 61.2 | 6
M06PU1050 | UF2 PLANT PERM PUMP | VSD | 5.5 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 5 | 1.2 | 61.2 | 14.5 | 14.5 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 48.672 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 14.5 | 0.33 | 8.9 | 2.5 | 61.2 | 10
M06PU1060 | UF2 PLANT PERM PHE HW PU | DOL | 3 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 5 | 1.2 | 61.2 | 12 | 12 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8113 | 45 | 0.94 | 5.2 | UNENCLOSED_TOUCHING | 1 | 28 | 87.9839 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 4.9 | 2.5 | 61.2 | 6
M06PU1093 | UF2 PLANT CIP BOOST PUMP | VSD | 11 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 5 | 1.2 | 61.2 | 14.5 | 14.5 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6413 | 45 | 0.94 | 18.8 | UNENCLOSED_TOUCHING | 2.5 | 28 | 24.336 | 2.5 | 2.5 |  | 2.5 | 20 |  | 20 | C | 130 | COPPER | 0.0225 | 2.5 | 2.5 | 78.6325 | PASS | 14.5 | 0.33 | 17.7 | 2.5 | 61.2 | 20
M06PU1100 | UF2 PLANT LOOP 1 PUMP | VSD | 30 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 5 | 1.2 | 56.4 | 20.3 | 20.3 | 0 | 20.3 | 0 | 20.3 | 0 | 20.3 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86 | 0.86 | 0 | 0.86 | 0 | 0.86 | 0 | 0.86 | 0.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.1125 | 45 | 0.94 | 51.2 | UNENCLOSED_TOUCHING | 16 | 28 | 9.6964 | 6 | 16 |  | 16 | 50 |  | 50 | C | 325 | COPPER | 0.0225 | 16 | 6 | 109.7995 | PASS | 20.3 | 0.86 | 48.2 | 16 | 56.4 | 50
M06PU1200 | UF2 PLANT LOOP 2 PUMP | VSD | 30 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 5 | 1.2 | 56.4 | 20.3 | 20.3 | 0 | 20.3 | 0 | 20.3 | 0 | 20.3 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86 | 0.86 | 0 | 0.86 | 0 | 0.86 | 0 | 0.86 | 0.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.1125 | 45 | 0.94 | 51.2 | UNENCLOSED_TOUCHING | 16 | 28 | 9.6964 | 6 | 16 |  | 16 | 50 |  | 50 | C | 325 | COPPER | 0.0225 | 16 | 6 | 109.7995 | PASS | 20.3 | 0.86 | 48.2 | 16 | 56.4 | 50
M07PU2011 | CRM TO PWDR 1 STD PUMP | VSD | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 5 | 1.2 | 50.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 0 | 14.5 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4056 | 45 | 0.94 | 2.6 | UNENCLOSED_TOUCHING | 1 | 28 | 213.6752 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 2.5 | 2.5 | 50.4 | 6
M07PU2012 | CRM TO PWDR 2 STD PUMP | VSD | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 5 | 1.2 | 50.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 0 | 14.5 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4056 | 45 | 0.94 | 2.6 | UNENCLOSED_TOUCHING | 1 | 28 | 213.6752 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 2.5 | 2.5 | 50.4 | 6
M07PU2013 | CRM TO CHEESE STD PUMP | VSD | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 5 | 1.2 | 50.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 0 | 14.5 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4056 | 45 | 0.94 | 2.6 | UNENCLOSED_TOUCHING | 1 | 28 | 213.6752 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 2.5 | 2.5 | 50.4 | 6
M07PU2014 | CRM TO ESL STD PUMP | VSD | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 5 | 1.2 | 50.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 0 | 14.5 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4056 | 45 | 0.94 | 2.6 | UNENCLOSED_TOUCHING | 1 | 28 | 213.6752 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 2.5 | 2.5 | 50.4 | 6
M07PU2097 | CRM SILOS CIPR PUMP | DOL | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 5 | 1.2 | 50.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 0 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0.21 | 0 | 0.21 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.0281 | 45 | 0.94 | 12.8 | UNENCLOSED_TOUCHING | 1.5 | 28 | 43.4028 | 2.5 | 2.5 |  | 2.5 | 16 |  | 16 | C | 104 | COPPER | 0.0225 | 2.5 | 2.5 | 98.2906 | PASS | 12 | 0.21 | 12.1 | 2.5 | 50.4 | 16
M07AG2102 | CRM SILO 1 AGITATOR | VSD | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 5 | 1.2 | 50.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 0 | 14.5 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59339 | 45 | 0.94 | 0.7 | UNENCLOSED_TOUCHING | 1 | 28 | 793.6508 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 0.6 | 2.5 | 50.4 | 6
M07AG2202 | CRM SILO 2 AGITATOR | VSD | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 5 | 1.2 | 50.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 0 | 14.5 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59339 | 45 | 0.94 | 0.7 | UNENCLOSED_TOUCHING | 1 | 28 | 793.6508 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 0.6 | 2.5 | 50.4 | 6
M07AG2302 | CRM SILO 3 AGITATOR | VSD | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 5 | 1.2 | 50.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 0 | 14.5 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59339 | 45 | 0.94 | 0.7 | UNENCLOSED_TOUCHING | 1 | 28 | 793.6508 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 0.6 | 2.5 | 50.4 | 6
M08PU2011 | LP SKIM TO PWDR 1 STD PUMP | DOL | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 1.2 | 39.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 75.2203 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 12 | 0.21 | 8.9 | 2.5 | 39.6 | 10
M08PU2012 | LP SKIM TO PWDR 2 STD PUMP | DOL | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 1.2 | 39.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 75.2203 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 12 | 0.21 | 8.9 | 2.5 | 39.6 | 10
M08PU2013 | LP SKIM TO CHEESE STD PUMP | DOL | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 1.2 | 39.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 75.2203 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 12 | 0.21 | 8.9 | 2.5 | 39.6 | 10
M08PU2014 | LP SKIM TO ESL STD PUMP | DOL | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 1.2 | 39.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.415 | 45 | 0.94 | 6.9 | UNENCLOSED_TOUCHING | 1 | 28 | 102.474 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 12 | 0.21 | 6.5 | 2.5 | 39.6 | 10
M08PU2097 | LP SKIM SILOS CIPR P | DOL | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 1.2 | 39.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.0281 | 45 | 0.94 | 12.8 | UNENCLOSED_TOUCHING | 1.5 | 28 | 55.2399 | 2.5 | 2.5 |  | 2.5 | 16 |  | 16 | C | 104 | COPPER | 0.0225 | 2.5 | 2.5 | 98.2906 | PASS | 12 | 0.21 | 12.1 | 2.5 | 39.6 | 16
M08AG2102 | LP SKIM SILO 1 AGITATOR | DOL | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 1.2 | 39.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7641 | 45 | 0.94 | 1.9 | UNENCLOSED_TOUCHING | 1 | 28 | 372.1425 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 1.8 | 2.5 | 39.6 | 6
M08AG2202 | LP SKIM SILO 2 AGITATOR | DOL | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 1.2 | 39.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7641 | 45 | 0.94 | 1.9 | UNENCLOSED_TOUCHING | 1 | 28 | 372.1425 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 1.8 | 2.5 | 39.6 | 6
M08AG2302 | LP SKIM SILO 3 AGITATOR | DOL | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 1.2 | 39.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7641 | 45 | 0.94 | 1.9 | UNENCLOSED_TOUCHING | 1 | 28 | 372.1425 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 1.8 | 2.5 | 39.6 | 6
M09PU2011 | HP SKIM TO PWDR 1 STD PUMP | VSD | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 0 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 5 | 1.2 | 55.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 0 | 14.5 | 0 | 0 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 53.9624 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 14.5 | 0.33 | 8.9 | 2.5 | 55.2 | 10
M09PU2012 | HP SKIM TO PWDR 2 STD PUMP | VSD | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 0 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 5 | 1.2 | 55.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 0 | 14.5 | 0 | 0 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 53.9624 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 14.5 | 0.33 | 8.9 | 2.5 | 55.2 | 10
M09PU2013 | HP SKIM TO CHEESE STD PUMP | VSD | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 0 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 5 | 1.2 | 55.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 0 | 14.5 | 0 | 0 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.415 | 45 | 0.94 | 6.9 | UNENCLOSED_TOUCHING | 1 | 28 | 73.514 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 14.5 | 0.33 | 6.5 | 2.5 | 55.2 | 10
M09PU2014 | HP SKIM TO ESL STD PUMP | VSD | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 0 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 5 | 1.2 | 55.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 0 | 14.5 | 0 | 0 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 53.9624 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 14.5 | 0.33 | 8.9 | 2.5 | 55.2 | 10
M09PU2097 | HP SKIM SILOS CIPR PUMP | DOL | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 0 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 5 | 1.2 | 55.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 0 | 12 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0.21 | 0 | 0.21 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.0281 | 45 | 0.94 | 12.8 | UNENCLOSED_TOUCHING | 1.5 | 28 | 39.6286 | 2.5 | 2.5 |  | 2.5 | 16 |  | 16 | C | 104 | COPPER | 0.0225 | 2.5 | 2.5 | 98.2906 | PASS | 12 | 0.21 | 12.1 | 2.5 | 55.2 | 16
M09AG2102 | HP SKIM SILO 1 AGITATOR | DOL | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 0 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 5 | 1.2 | 55.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 0 | 12 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0.21 | 0 | 0.21 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88206 | 45 | 0.94 | 1 | UNENCLOSED_TOUCHING | 1 | 28 | 507.2464 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 0.9 | 2.5 | 55.2 | 6
M09AG2202 | HP SKIM SILO 2 AGITATOR | DOL | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 0 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 5 | 1.2 | 55.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 0 | 12 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0.21 | 0 | 0.21 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88206 | 45 | 0.94 | 1 | UNENCLOSED_TOUCHING | 1 | 28 | 507.2464 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 0.9 | 2.5 | 55.2 | 6
C01PU4810 | CHEESE MILK PAST FEED PUMP | VSD | 5.5 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 5 | 1.2 | 67.2 | 14.5 | 14.5 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 44.3262 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 14.5 | 0.33 | 8.9 | 2.5 | 67.2 | 10
C01PU4815 | CHEESE MILK PAST TIMING PUMP | VSD | 5.5 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 5 | 1.2 | 67.2 | 14.5 | 14.5 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 44.3262 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 14.5 | 0.33 | 8.9 | 2.5 | 67.2 | 10
C01PU4880 | CHEESE MILK PAST HW PUMP | DOL | 5.5 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 5 | 1.2 | 67.2 | 12 | 12 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 44.3262 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 12 | 0.21 | 8.9 | 2.5 | 67.2 | 10
M10PU2011 | LOADOUT SILOS TO LOAD OUT PUMP | VSD | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 5 | 1.2 | 79.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5 | 0 | 16.5 | 0 | 0 | 0 | 16.5 | 0 | 16.5 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0 | 0.41 | 0 | 0 | 0 | 0.41 | 0 | 0.41 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6413 | 45 | 0.94 | 18.8 | UNENCLOSED_TOUCHING | 2.5 | 28 | 18.8051 | 2.5 | 2.5 | 4 | 4 | 20 |  | 20 | C | 130 | COPPER | 0.0225 | 4 | 2.5 | 96.7784 | PASS | 16.5 | 0.41 | 17.7 | 4 | 79.2 | 20
M10PU2012 | LOADOUT SILOS TO PWDR1 STD PUMP | DOL | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 5 | 1.2 | 79.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.415 | 45 | 0.94 | 6.9 | UNENCLOSED_TOUCHING | 1 | 28 | 51.237 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 12 | 0.21 | 6.5 | 2.5 | 79.2 | 10
M10PU2097 | LOADOUT SILOS CIPR PUMP | DOL | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 5 | 1.2 | 79.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.0281 | 45 | 0.94 | 12.8 | UNENCLOSED_TOUCHING | 1.5 | 28 | 27.6199 | 2.5 | 2.5 |  | 2.5 | 16 |  | 16 | C | 104 | COPPER | 0.0225 | 2.5 | 2.5 | 98.2906 | PASS | 12 | 0.21 | 12.1 | 2.5 | 79.2 | 16
M10AG2102 | LOADOUT SILO 1 AGITATOR | DOL | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 5 | 1.2 | 79.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59339 | 45 | 0.94 | 0.7 | UNENCLOSED_TOUCHING | 1 | 28 | 505.0505 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 0.6 | 2.5 | 79.2 | 6
M10AG2202 | LOADOUT SILO 2 AGITATOR | DOL | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 5 | 1.2 | 79.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59339 | 45 | 0.94 | 0.7 | UNENCLOSED_TOUCHING | 1 | 28 | 505.0505 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 0.6 | 2.5 | 79.2 | 6
A01PU2011 | ESL TKS TO FILLER 1 PUMP | VSD | 5.5 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 9 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 5 | 1.2 | 70.8 | 14.5 | 14.5 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 14.5 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 42.0724 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 14.5 | 0.33 | 8.9 | 2.5 | 70.8 | 10
A01PU2012 | ESL TKS TO FILLER 2 PUMP | VSD | 5.5 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 9 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 5 | 1.2 | 70.8 | 14.5 | 14.5 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 14.5 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 42.0724 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 14.5 | 0.33 | 8.9 | 2.5 | 70.8 | 10
A01PU2013 | ESL TKS TO ESL LOADOUT PUMP | VSD | 5.5 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 9 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 5 | 1.2 | 70.8 | 14.5 | 14.5 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 14.5 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8206 | 45 | 0.94 | 9.4 | UNENCLOSED_TOUCHING | 1 | 28 | 42.0724 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 14.5 | 0.33 | 8.9 | 2.5 | 70.8 | 10
B01PU2031 | CRM CRYST TKS TO BUTTER PLANT PUMP | VSD | 2.2 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 9 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 5 | 1.2 | 70.8 | 14.5 | 14.5 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 14.5 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5283 | 45 | 0.94 | 3.8 | UNENCLOSED_TOUCHING | 1 | 28 | 104.0737 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 3.6 | 2.5 | 70.8 | 6
A01PU2097 | CRM CRIST/ESL/DUAL TKS CIPR PUMP | DOL | 7.5 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 9 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 5 | 1.2 | 70.8 | 12 | 12 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.0281 | 45 | 0.94 | 12.8 | UNENCLOSED_TOUCHING | 1.5 | 28 | 30.8969 | 2.5 | 2.5 |  | 2.5 | 16 |  | 16 | C | 104 | COPPER | 0.0225 | 2.5 | 2.5 | 98.2906 | PASS | 12 | 0.21 | 12.1 | 2.5 | 70.8 | 16
B01AG2102 | CRM CRIST TK 1 AGITATOR | VSD | 2.2 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 9 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 5 | 1.2 | 76.8 | 14.5 | 14.5 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5283 | 45 | 0.94 | 3.8 | UNENCLOSED_TOUCHING | 1 | 28 | 95.943 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 3.6 | 2.5 | 76.8 | 6
A01AG2102 | ESL TK 1 AGITATOR | DOL | 0.75 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 9 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 5 | 1.2 | 76.8 | 12 | 12 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2028 | 45 | 0.94 | 1.3 | UNENCLOSED_TOUCHING | 1 | 28 | 280.4487 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 1.3 | 2.5 | 76.8 | 6
B01AG2202 | CRM CRIST TK 2 AGITATOR | VSD | 2.2 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 9 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 5 | 1.2 | 76.8 | 14.5 | 14.5 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5283 | 45 | 0.94 | 3.8 | UNENCLOSED_TOUCHING | 1 | 28 | 95.943 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 3.6 | 2.5 | 76.8 | 6
A01AG2202 | ESL TK 2 AGITATOR | DOL | 0.75 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 9 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 5 | 1.2 | 76.8 | 12 | 12 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2028 | 45 | 0.94 | 1.3 | UNENCLOSED_TOUCHING | 1 | 28 | 280.4487 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 1.3 | 2.5 | 76.8 | 6
B01AG2402 | CRM CRYST TK 3 AGITATOR | VSD | 2.2 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 9 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 5 | 1.2 | 76.8 | 14.5 | 14.5 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5283 | 45 | 0.94 | 3.8 | UNENCLOSED_TOUCHING | 1 | 28 | 95.943 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 3.6 | 2.5 | 76.8 | 6
U01PU3410 | CIP SET 1 CIPS 1 PUMP | VSD | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 0 | 12 | 0 | 20 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 5 | 1.2 | 105.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4 | 0 | 18.4 | 0 | 0 | 0 | 18.4 | 0 | 18.4 | 0 | 18.4 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62 | 0.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62 | 0 | 0.62 | 0 | 0 | 0 | 0.62 | 0 | 0.62 | 0 | 0.62 | 0.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.0563 | 45 | 0.94 | 25.6 | UNENCLOSED_TOUCHING | 4 | 28 | 10.3575 | 4 | 4 | 10 | 10 | 25 |  | 25 | C | 162.5 | COPPER | 0.0225 | 10 | 4 | 143.7851 | PASS | 18.4 | 0.62 | 24.1 | 10 | 105.6 | 25
U01PU3420 | CIP SET 1 CIPS 2 PUMP | VSD | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 0 | 12 | 0 | 20 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 5 | 1.2 | 105.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4 | 0 | 18.4 | 0 | 0 | 0 | 18.4 | 0 | 18.4 | 0 | 18.4 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62 | 0.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62 | 0 | 0.62 | 0 | 0 | 0 | 0.62 | 0 | 0.62 | 0 | 0.62 | 0.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.0563 | 45 | 0.94 | 25.6 | UNENCLOSED_TOUCHING | 4 | 28 | 10.3575 | 4 | 4 | 10 | 10 | 25 |  | 25 | C | 162.5 | COPPER | 0.0225 | 10 | 4 | 143.7851 | PASS | 18.4 | 0.62 | 24.1 | 10 | 105.6 | 25
U01PU3513 | CIP SET 1 CAUSTIC TK RECIRC PUMP | DOL | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 0 | 12 | 0 | 20 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 5 | 1.2 | 105.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.415 | 45 | 0.94 | 6.9 | UNENCLOSED_TOUCHING | 1 | 28 | 38.4278 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 12 | 0.21 | 6.5 | 2.5 | 105.6 | 10
U01PU3613 | CIP SET 1 ACID TK RECIRC PUMP | DOL | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 0 | 12 | 0 | 20 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 5 | 1.2 | 105.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.415 | 45 | 0.94 | 6.9 | UNENCLOSED_TOUCHING | 1 | 28 | 38.4278 | 2.5 | 2.5 |  | 2.5 | 10 |  | 10 | C | 65 | COPPER | 0.0225 | 2.5 | 2.5 | 157.265 | PASS | 12 | 0.21 | 6.5 | 2.5 | 105.6 | 10
U06PU4340 | CONDENSATE RETURN PUMP | DOL | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 0 | 12 | 0 | 20 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 5 | 1.2 | 105.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0 | 0 | 0.21 | 0 | 0.21 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5283 | 45 | 0.94 | 3.8 | UNENCLOSED_TOUCHING | 1 | 28 | 69.7767 | 2.5 | 2.5 | 2.5 | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 3.6 | 2.5 | 105.6 | 6
B01MC0001 | BUTTER EGLI OEM | LOAD | 75 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 9 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 5 | 1.2 | 86.4 | 41 | 41 | 0 | 41 | 0 | 41 | 0 | 0 | 0 | 41 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.86 | 3.86 | 0 | 3.86 | 0 | 3.86 | 0 | 3.86 | 0 | 3.86 | 0 | 0 | 3.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.2813 | 45 | 0.94 | 128 | UNENCLOSED_TOUCHING | 50 | 28 | 2.5318 | 16 | 50 | 70 | 70 | 125 | 160 | 160 | C | 1040 | COPPER | 0.0225 | 70 | 25 | 144.8493 | PASS | 41 | 3.86 | 120.3 | 70 | 86.4 | 160
A02MC0001 | ESL DS TRIPLE OEM | LOAD | 87 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 14 | 0 | 2 | 0 | 3 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 5 | 1.2 | 67.2 | 41 | 41 | 0 | 41 | 0 | 41 | 0 | 0 | 0 | 41 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.86 | 3.86 | 0 | 3.86 | 0 | 3.86 | 0 | 3.86 | 0 | 3.86 | 3.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139.5263 | 45 | 0.94 | 148.5 | UNENCLOSED_TOUCHING | 70 | 28 | 2.8058 | 16 | 70 |  | 70 | 160 | 200 | 200 | C | 1300 | COPPER | 0.0225 | 70 | 25 | 115.8794 | PASS | 41 | 3.86 | 139.6 | 70 | 67.2 | 200
M03SC2402 | EXTRA AGITATOR VSD #1 | VSD | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 5 | 1.2 | 63.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 0 | 14.5 | 0 | 0 | 0 | 14.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7641 | 45 | 0.94 | 1.9 | UNENCLOSED_TOUCHING | 1 | 28 | 231.7114 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 14.5 | 0.33 | 1.8 | 2.5 | 63.6 | 6
M07AG2402 | EXTRA AGITATOR DOL #1 | DOL | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 5 | 1.2 | 50.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 0 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0.21 | 0 | 0.21 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59339 | 45 | 0.94 | 0.7 | UNENCLOSED_TOUCHING | 1 | 28 | 793.6508 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 0.6 | 2.5 | 50.4 | 6
M09AG2302 | EXTRA AGITATOR DOL #2 | DOL | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 5 | 0 | 7 | 0 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 5 | 1.2 | 55.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 0 | 12 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0.21 | 0.21 | 0 | 0.21 | 0 | 0 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88206 | 45 | 0.94 | 1 | UNENCLOSED_TOUCHING | 1 | 28 | 507.2464 | 2.5 | 2.5 |  | 2.5 | 6 |  | 6 | C | 39 | COPPER | 0.0225 | 2.5 | 2.5 | 262.1083 | PASS | 12 | 0.21 | 0.9 | 2.5 | 55.2 | 6

## SEGMENTS
SEG_ID | HORIZONTAL | VERTICAL | LENGTH | INITIAL_DIAMETER | LAYERS | X_CAPACITY | MIN_TRAYWIDTH | SELECTED_TRAY | TRAY_OVERIDE | TRAY_MASS | SPAN_BRACE | CABLE_TOTAL | TRAY_LENGTH | CABLE_TRAY
SEG1 | 10 | 3 | 13 | 660.1 | 2 | 1.2 | 396.06 | 450mm | 600mm | 23.45 | 6m | 41 | 13 | 600mm
SEG2 | 2 | 0 | 2 | 660.1 | 2 | 1.2 | 396.06 | 450mm | 600mm | 23.45 | 6m | 41 | 2 | 600mm
SEG3 | 10 | 6 | 16 | 106 | 2 | 1.2 | 63.6 | 150mm |  | 2.16 | 6m | 8 | 16 | 150mm
SEG4 | 14 | 0 | 14 | 481.7 | 2 | 1.2 | 289.02 | 300mm | 600mm | 18.03 | 6m | 29 | 14 | 600mm
SEG5 | 2 | 6 | 8 | 110.6 | 2 | 1.2 | 66.36 | 150mm |  | 3.25 | 6m | 7 | 8 | 150mm
SEG6 | 2 | 0 | 2 | 411.7 | 2 | 1.2 | 247.02 | 300mm | 450mm | 16.5 | 6m | 24 | 2 | 450mm
SEG7 | 2 | 6 | 8 | 40.6 | 2 | 1.2 | 24.36 | 150mm |  | 1.72 | 6m | 2 | 8 | 150mm
SEG8 | 3 | 0 | 3 | 40.6 | 2 | 1.2 | 24.36 | 150mm | 450mm | 14.78 | 6m | 22 | 3 | 450mm
SEG9 | 2 | 6 | 8 | 40.6 | 2 | 1.2 | 24.36 | 150mm |  | 1.72 | 6m | 2 | 8 | 150mm
SEG10 | 9 | 0 | 9 | 219.5 | 2 | 1.2 | 131.7 | 150mm | 300mm | 10.66 | 6m | 12 | 9 | 300mm
SEG11 | 2 | 6 | 8 | 41 | 2 | 1.2 | 24.6 | 150mm |  | 3.86 | 6m | 1 | 8 | 150mm
SEG12 | 10 | 6 | 16 | 67.5 | 2 | 1.2 | 40.5 | 150mm |  | 1.41 | 6m | 5 | 16 | 150mm
SEG13 | 3 | 0 | 3 | 111 | 2 | 1.2 | 66.6 | 150mm | 300mm | 5.39 | 6m | 6 | 3 | 300mm
SEG14 | 4 | 0 | 4 | 111 | 2 | 1.2 | 66.6 | 150mm | 450mm | 2.4 | 6m | 8 | 4 | 450mm
SEG15 | 2 | 6 | 8 | 70 | 2 | 1.2 | 42 | 150mm |  | 1.53 | 6m | 5 | 8 | 150mm
SEG16 | 7 | 6 | 13 | 41 | 2 | 1.2 | 24.6 | 150mm | 300mm | 0.87 | 6m | 3 | 13 | 300mm
SEG17 | 9 | 0 | 9 | 0 | 2 | 1.2 | 0 |  | 300mm | 0 | 6m | 0 | 9 | 300mm
SEG18 | 5 | 6 | 11 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 11 | NOT IN USE
SEG19 | 4 | 0 | 4 | 0 | 2 | 1.2 | 0 |  | 300mm | 0 | 6m | 0 | 4 | 300mm
SEG20 | 5 | 6 | 11 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 11 | NOT IN USE
SEG21 | 4 | 0 | 4 | 72.4 | 2 | 1.2 | 43.44 | 150mm | 600mm | 3.26 | 6m | 4 | 4 | 600mm
SEG22 | 10 | 6 | 16 | 72.4 | 2 | 1.2 | 43.44 | 150mm |  | 3.26 | 6m | 4 | 16 | 150mm
SEG23 | 2 | 6 | 8 | 70 | 2 | 1.2 | 42 | 150mm |  | 1.53 | 6m | 5 | 8 | 150mm
SEG24 | 15 | 6 | 21 | 41 | 2 | 1.2 | 24.6 | 150mm | 300mm | 3.86 | 6m | 1 | 21 | 300mm
SEG25 | 0 | 0 | 0 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 0 | NOT IN USE
SEG26 | 0 | 0 | 0 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 0 | NOT IN USE
SEG27 | 0 | 0 | 0 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 0 | NOT IN USE
SEG28 | 0 | 0 | 0 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 0 | NOT IN USE
SEG29 | 0 | 0 | 0 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 0 | NOT IN USE
SEG30 | 4 | 2 | 6 | 603.6 | 2 | 1.2 | 362.16 | 450mm | 600mm | 12.8 | 6m | 45 | 6 | 600mm
SEG31 | 3 | 0 | 3 | 603.6 | 2 | 1.2 | 362.16 | 450mm |  | 12.8 | 6m | 45 | 3 | 450mm
SEG32 | 5 | 0 | 5 | 231.5 | 2 | 1.2 | 138.9 | 150mm | 450mm | 4.89 | 6m | 17 | 5 | 450mm
SEG33 | 2 | 5 | 7 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 7 | NOT IN USE
SEG34 | 7 | 0 | 7 | 231.5 | 2 | 1.2 | 138.9 | 150mm | 450mm | 4.89 | 6m | 17 | 7 | 450mm
SEG35 | 2 | 5 | 7 | 125.5 | 2 | 1.2 | 75.3 | 150mm |  | 2.73 | 6m | 9 | 7 | 150mm
SEG36 | 9 | 0 | 9 | 125.5 | 2 | 1.2 | 75.3 | 150mm |  | 2.73 | 6m | 9 | 9 | 150mm
SEG37 | 5 | 0 | 5 | 106 | 2 | 1.2 | 63.6 | 150mm | 450mm | 2.16 | 6m | 8 | 5 | 450mm
SEG38 | 10 | 5 | 15 | 106 | 2 | 1.2 | 63.6 | 150mm |  | 2.16 | 6m | 8 | 15 | 150mm
SEG39 | 8 | 0 | 8 | 372.1 | 2 | 1.2 | 223.26 | 300mm | 450mm | 7.91 | 6m | 28 | 8 | 450mm
SEG40 | 6 | 5 | 11 | 96 | 2 | 1.2 | 57.6 | 150mm |  | 1.68 | 6m | 8 | 11 | 150mm
SEG41 | 8 | 0 | 8 | 276.1 | 2 | 1.2 | 165.66 | 300mm | 450mm | 6.23 | 6m | 20 | 8 | 450mm
SEG42 | 22 | 0 | 22 | 52.3 | 2 | 1.2 | 31.38 | 150mm |  | 1.52 | 6m | 3 | 22 | 150mm
SEG43 | 10 | 0 | 10 | 35.8 | 2 | 1.2 | 21.48 | 150mm |  | 1.11 | 6m | 2 | 10 | 150mm
SEG44 | 9 | 5 | 14 | 18.4 | 2 | 1.2 | 11.04 | 150mm |  | 0.62 | 6m | 1 | 14 | 150mm
SEG45 | 9 | 0 | 9 | 223.8 | 2 | 1.2 | 134.28 | 150mm | 450mm | 4.71 | 6m | 17 | 9 | 450mm
SEG46 | 9 | 5 | 14 | 86.5 | 2 | 1.2 | 51.9 | 150mm |  | 1.59 | 6m | 7 | 14 | 150mm
SEG47 | 12 | 0 | 12 | 137.3 | 2 | 1.2 | 82.38 | 150mm | 450mm | 3.12 | 6m | 10 | 12 | 450mm
SEG48 | 10 | 5 | 15 | 64.5 | 2 | 1.2 | 38.7 | 150mm |  | 1.25 | 6m | 5 | 15 | 150mm
SEG49 | 20 | 0 | 20 | 72.8 | 2 | 1.2 | 43.68 | 150mm | 450mm | 1.87 | 6m | 5 | 20 | 450mm
SEG50 | 12 | 5 | 17 | 72.8 | 2 | 1.2 | 43.68 | 150mm |  | 1.87 | 6m | 5 | 17 | 150mm
SEG51 | 2 | 5 | 7 | 17.4 | 2 | 1.2 | 10.44 | 150mm |  | 0.49 | 6m | 1 | 7 | 150mm
SEG52 | 0 | 0 | 0 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 0 | NOT IN USE
SEG53 | 0 | 0 | 0 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 0 | NOT IN USE
SEG54 | 0 | 0 | 0 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 0 | NOT IN USE
SEG55 | 0 | 0 | 0 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 0 | NOT IN USE
SEG56 | 0 | 0 | 0 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 0 | NOT IN USE
SEG57 | 0 | 0 | 0 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 0 | NOT IN USE
SEG58 | 0 | 0 | 0 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 0 | NOT IN USE
SEG59 | 0 | 0 | 0 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 0 | NOT IN USE
SEG60 | 0 | 0 | 0 | 0 | 2 | 1.2 | 0 |  |  | 0 | 6m | 0 | 0 | NOT IN USE

## DATA
Default Power Factor | 0.9 | AMBIENT_TEMP | CONSTANT (K) |  | MM^2 | AMP_SPACED_RAW | AMP_SPACED | AMP_TOUCHING_RAW | AMP_TOUCHING |  | INSTALL_METHOD | AMBIENT | DERATE | MM^2 | Vc | MM^2 | DIAMETER | MASS | MM^2 | DIAMETER | MASS | MM^2 | DIAMETER | MASS | LOAD TYPE | LAYERS | WIDTH | PART_NUMBER | LOADING | BRACE_SPAN | DEVICE | DEVICE_CURVE | MULTIPLIER | CONDUCTOR_MATERIAL | CONSTANT | MM^2 | EARTH
|  | 60 | 111 | 0 | 500 | 779 | 623.2 | 718 | 574.4 |  | UNENCLOSED_SPACED | 60 | 0.73 | 500 | 0.156 | 300 | 63.5 | 11.53 | 120 | 41.3 | 4.42 | 150 | 49 | 6.65 | VSD | 1 | 9999999 | ERROR | 810 | 2m | 250 | B | 3.5 | COPPER | 0.0225 | 500 | 120
System Voltage | 400 | 55 | 115 | 1 | 400 | 685 | 548 | 632 | 505.6 |  | UNENCLOSED_TOUCHING | 55 | 0.81 | 400 | 0.168 | 240 | 57.2 | 9.15 | 95 | 37.4 | 3.63 | 120 | 46 | 5.43 | DOL | 2 | 900 | 900mm | 370 | 3m | 200 | C | 6.5 | ALUMINIUM | 0.036 | 400 | 120
|  | 50 | 118 | 2 | 300 | 594 | 475.2 | 549 | 439.2 |  |  | 50 | 0.88 | 300 | 0.186 | 185 | 50.8 | 7.03 | 70 | 33.1 | 2.68 | 95 | 43 | 4.36 | LOAD |  | 750 | 750mm | 175 | 4m | 160 | D | 12.5 |  |  | 300 | 120
Maximum Voltage Drop % | 0.07 | 45 | 122 | 3 | 240 | 517 | 413.6 | 479 | 383.2 |  |  | 45 | 0.94 | 240 | 0.21 | 150 | 45.8 | 5.82 | 50 | 28.2 | 2 | 70 | 41 | 3.86 |  |  | 600 | 600mm | 125 | 5m | 125 |  |  |  |  | 240 | 95
|  | 40 | 126 | 4 | 185 | 240 | 192 | 404 | 323.2 |  |  | 40 | 1 | 185 | 0.251 | 120 | 42 | 4.65 | 35 | 25.4 | 1.44 | 50 | 35.1 | 2.76 |  |  | 450 | 450mm | 90 | 6m | 100 |  |  |  |  | 185 | 70
Copper Constant | 0.0225 | K VALUES FOR COPPER AT AMBIENT TEMP |  | 5 | 150 | 377 | 301.6 | 350 | 280 |  |  |  |  | 150 | 0.296 | 95 | 36.9 | 3.85 | 25 | 22.1 | 1.05 | 35 | 31 | 1.98 |  |  | 300 | 300mm |  |  | 80 |  |  |  |  | 150 | 50
|  | TABLE 52 OF ASNZS 3008.1.1-2017 |  | 6 | 120 | 330 | 264 | 306 | 244.8 |  |  |  |  | 120 | 0.351 | 70 | 32.1 | 2.8 | 16 | 18.9 | 0.71 | 25 | 26.8 | 1.46 |  |  | 150 | 150mm |  |  | 63 |  |  |  |  | 120 | 35
Aluminium Constant | 0.036 |  |  | 7 | 95 | 283 | 226.4 | 263 | 210.4 |  |  |  |  | 95 | 0.431 | 50 | 28.8 | 2.15 | 10 | 16.6 | 0.48 | 16 | 22.1 | 0.97 |  |  | 0 |  |  |  | 50 |  |  |  |  | 95 | 25
|  |  |  | 8 | 70 | 229 | 183.2 | 213 | 170.4 |  |  |  |  | 70 | 0.583 | 35 | 25.6 | 1.62 | 6 | 14.5 | 0.33 | 10 | 19.2 | 0.67 | [6 empty] | 40 |  |  |  |  | 70 | 25
Phase Voltage | 230 |  |  | 9 | 50 | 180 | 144 | 168 | 134.4 |  |  |  |  | 50 | 0.829 | 25 | 22.8 | 1.22 | 4 | 13.5 | 0.29 | 6 | 17.5 | 0.44 | [6 empty] | 32 |  |  |  |  | 50 | 16
|  |  |  | 10 | 35 | 147 | 117.6 | 137 | 109.6 |  |  |  |  | 35 | 1.11 | 16 | 20.3 | 0.86 | 2.5 | 12 | 0.21 | 4 | 15.5 | 0.34 | [6 empty] | 25 |  |  |  |  | 35 | 10
|  |  |  | 11 | 25 | 119 | 95.2 | 111 | 88.8 |  |  |  |  | 25 | 1.54 | 10 | 18.4 | 0.62 |  |  |  | 2.5 | 13.4 | 0.23 | [6 empty] | 20 |  |  |  |  | 25 | 6
|  |  |  | 12 | 16 | 88 | 70.4 | 83 | 66.4 |  |  |  |  | 16 | 2.43 | 6 | 17.4 | 0.49 | [12 empty] | 16 |  |  |  |  | 16 | 6
|  |  |  | 13 | 10 | 66 | 52.8 | 62 | 49.6 |  |  |  |  | 10 | 3.86 | 4 | 16.5 | 0.41 | [12 empty] | 10 |  |  |  |  | 10 | 4
|  |  |  | 14 | 6 | 48 | 38.4 | 45 | 36 |  |  |  |  | 6 | 6.49 | 2.5 | 14.5 | 0.33 | [12 empty] | 6 |  |  |  |  | 6 | 2.5
|  |  |  | 15 | 4 | 38 | 30.4 | 35 | 28 |  |  |  |  | 4 | 9.71 | [20 empty] | 4 | 2.5
|  |  |  | 16 | 2.5 | 28 | 22.4 | 26 | 20.8 |  |  |  |  | 2.5 | 15.6 | [20 empty] | 2.5 | 2.5
|  |  |  | 17 | 1.5 | 20 | 16 | 19 | 15.2 |  |  |  |  | 2.5 | 28.6 | [20 empty] | 1.5 | 1.5
|  |  |  | 18 | 1 | 16 | 12.8 | 14 | 11.2 |  |  |  |  | 2.5 | 44.7 | [20 empty] | 1 | 1
current carrying capacity
[5 empty] | TABLE 14 OF ASNZ 3008.1.1-2017 | [6 empty] | ambient temperature derating |  | voltage drop Vc |  | vsd cable spec |  |  | dol cable spec | [5 empty] | vsd = shielded 3C+E | cable layering | Cable Tray Spec |  | choose span to fit mass loading |  |  | protective device curve |  | conductor material |  | earth conductor size
[12 empty] | TABLE 27(1) OF ASNZ 3008.1.1-2017 |  |  |  | used olflex VAROLEX 3C+E |  |  | used olflex VERSOLEX 3C+E | [5 empty] | dol = 3C+E | allow single layer | used unistrut AL20 cable ladder |  | used unistrut AL20 cable ladder |  | protective device
[16 empty] | mass is kg per 1m |  |  | mass is kg per 1m | [5 empty] | load = 4C+E | allow double layer | 6m lengths
load cable spec
used olflex VERSOLEX 4C+E
mass is kg per 1m
|  |  |  | "0"= | [500, | 779, |  | 718] |  | "0"=[500,779,718]
|  |  |  | "1"= | [400, | 685, |  | 632] |  | "1"=[400,685,632]
|  |  |  | "2"= | [300, | 594, |  | 549] |  | "2"=[300,594,549] | [11 empty] | note: no VERSOLEX > 95mm2
|  |  |  | "3"= | [240, | 517, |  | 479] |  | "3"=[240,517,479] | [11 empty] | Using alternative values
|  |  |  | "4"= | [185, | 240, |  | 404] |  | "4"=[185,240,404]
|  |  |  | "5"= | [150, | 377, |  | 350] |  | "5"=[150,377,350]
|  |  |  | "6"= | [120, | 330, |  | 306] |  | "6"=[120,330,306]
|  |  |  | "7"= | [95, | 283, |  | 263] |  | "7"=[95,283,263]
|  |  |  | "8"= | [70, | 229, |  | 213] |  | "8"=[70,229,213]
|  |  |  | "9"= | [50, | 180, |  | 168] |  | "9"=[50,180,168]
|  |  |  | "10"= | [35, | 147, |  | 137] |  | "10"=[35,147,137]
|  |  |  | "11"= | [25, | 119, |  | 111] |  | "11"=[25,119,111]
|  |  |  | "12"= | [16, | 88, |  | 83] |  | "12"=[16,88,83]
|  |  |  | "13"= | [10, | 66, |  | 62] |  | "13"=[10,66,62]
|  |  |  | "14"= | [6, | 48, |  | 45] |  | "14"=[6,48,45]
|  |  |  | "15"= | [4, | 38, |  | 35] |  | "15"=[4,38,35]
|  |  |  | "16"= | [2.5, | 28, |  | 26] |  | "16"=[2.5,28,26]
|  |  |  | "17"= | [1.5, | 20, |  | 19] |  | "17"=[1.5,20,19]
|  |  |  | "18"= | [1, | 16, |  | 14] |  | "18"=[1,16,14]
|  |  |  | = | [, | , |  | ] |  | = [,,]
|  |  |  | = | [current carrying capacity, | , |  | ] |  | = [current carrying capacity,,]
|  |  |  | = | [TABLE 14 OF ASNZ 3008.1.1-2017, | , |  | ] |  | = [TABLE 14 OF ASNZ 3008.1.1-2017,,]
|  |  |  | = | [, | , |  | ] |  | = [,,]

## V1-V2-COMPARISON
CABLE | DESCRIPTION | V1-NZ | V2-AUS | CHANGE | NOTE_1 | NOTE_2
M01PU1121 | LOADIN 1 SILOS PUMP 1 | 4 | 4 | NO
M02PU1121 | LOADIN 2 SILOS PUMP 1 | 6 | 6 | NO
M02PU1122 | LOADIN 2 SILOS PUMP 2 | 10 | 10 | NO
M03PU2011 | RM SILOS TO SEP 1 PUMP | 2.5 | 2.5 | NO
M03PU2012 | RM SILOS TO SEP 2 PUMP | 2.5 | 2.5 | NO
M03PU2097 | RM SILOS CIPR PUMP | 4 | 2.5 | YES | 4mm^2 -> 2.5mm^2 | Cable reduced due to increased voltage drop allowance
M03AG2102 | RM SILO 1 AGITATOR | 2.5 | 2.5 | NO
M03AG2202 | RM SILO 2 AGITATOR | 2.5 | 2.5 | NO
M03AG2302 | RM SILO 3 AGITATOR | 2.5 | 2.5 | NO
M15PU3110 | SEP 1 FEED PUMP | 2.5 | 2.5 | NO
M15CC3120 | SEP 1 SEPARATOR | 35 | 35 | NO
M15PU3150 | SEP 1 CREAM PUMP | 2.5 | 2.5 | NO
M15PU3158 | LP SKIM 1 TRANSFER PUMP | 2.5 | 2.5 | NO
M15PU3160 | SEP 1 CREAM PHE CHW PUMP | 2.5 | 2.5 | NO
M15PU3180 | SEP 1 PHE HW PUMP | 2.5 | 2.5 | NO
M16PU3110 | SEP 2 FEED PUMP | 2.5 | 2.5 | NO
M16CC3120 | SEP 2 SEPARATOR | 25 | 25 | NO
M16PU3150 | SEP 2 CREAM PUMP | 2.5 | 2.5 | NO
M16PU3158 | LP SKIM 2 TRANSFER PUMP | 2.5 | 2.5 | NO
M16PU3160 | SEP 2 CREAM PHE CHW PUMP | 2.5 | 2.5 | NO
M16PU3180 | SEP 2 PHE HW PUMP | 2.5 | 2.5 | NO
M05PU1027 | UF1 PLANT FEED PUMP | 2.5 | 2.5 | NO
M05PU1038 | UF1 PLANT RET PUMP | 2.5 | 2.5 | NO
M05PU1050 | UF1 PLANT PERM PUMP | 2.5 | 2.5 | NO
M05PU1060 | UF1 PLANT PERM PHE HW PUMP | 2.5 | 2.5 | NO
M05PU1093 | UF1 PLANT CIP BOOST PUMP | 2.5 | 2.5 | NO
M05PU1100 | UF1 PLANT LOOP 1 PUMP | 10 | 16 | YES | 10mm^2 -> 16mm^2 | Cable increased due to increased safety margin
M05PU1200 | UF1 PLANT LOOP 2 PUMP | 10 | 16 | YES | 10mm^2 -> 16mm^2 | Cable increased due to increased safety margin
M06PU1027 | UF2 PLANT FEED PUMP | 2.5 | 2.5 | NO
M06PU1038 | UF2 PLANT RET PUMP | 2.5 | 2.5 | NO
M06PU1050 | UF2 PLANT PERM PUMP | 2.5 | 2.5 | NO
M06PU1060 | UF2 PLANT PERM PHE HW PU | 2.5 | 2.5 | NO
M06PU1093 | UF2 PLANT CIP BOOST PUMP | 2.5 | 2.5 | NO
M06PU1100 | UF2 PLANT LOOP 1 PUMP | 10 | 16 | YES | 10mm^2 -> 16mm^2 | Cable increased due to increased safety margin
M06PU1200 | UF2 PLANT LOOP 2 PUMP | 10 | 16 | YES | 10mm^2 -> 16mm^2 | Cable increased due to increased safety margin
M07PU2011 | CRM TO PWDR 1 STD PUMP | 2.5 | 2.5 | NO
M07PU2012 | CRM TO PWDR 2 STD PUMP | 2.5 | 2.5 | NO
M07PU2013 | CRM TO CHEESE STD PUMP | 2.5 | 2.5 | NO
M07PU2014 | CRM TO ESL STD PUMP | 2.5 | 2.5 | NO
M07PU2097 | CRM SILOS CIPR PUMP | 2.5 | 2.5 | NO
M07AG2102 | CRM SILO 1 AGITATOR | 2.5 | 2.5 | NO
M07AG2202 | CRM SILO 2 AGITATOR | 2.5 | 2.5 | NO
M07AG2302 | CRM SILO 3 AGITATOR | 2.5 | 2.5 | NO
M08PU2011 | LP SKIM TO PWDR 1 STD PUMP | 2.5 | 2.5 | NO
M08PU2012 | LP SKIM TO PWDR 2 STD PUMP | 2.5 | 2.5 | NO
M08PU2013 | LP SKIM TO CHEESE STD PUMP | 2.5 | 2.5 | NO
M08PU2014 | LP SKIM TO ESL STD PUMP | 2.5 | 2.5 | NO
M08PU2097 | LP SKIM SILOS CIPR P | 2.5 | 2.5 | NO
M08AG2102 | LP SKIM SILO 1 AGITATOR | 2.5 | 2.5 | NO
M08AG2202 | LP SKIM SILO 2 AGITATOR | 2.5 | 2.5 | NO
M08AG2302 | LP SKIM SILO 3 AGITATOR | 2.5 | 2.5 | NO
M09PU2011 | HP SKIM TO PWDR 1 STD PUMP | 2.5 | 2.5 | NO
M09PU2012 | HP SKIM TO PWDR 2 STD PUMP | 2.5 | 2.5 | NO
M09PU2013 | HP SKIM TO CHEESE STD PUMP | 2.5 | 2.5 | NO
M09PU2014 | HP SKIM TO ESL STD PUMP | 2.5 | 2.5 | NO
M09PU2097 | HP SKIM SILOS CIPR PUMP | 2.5 | 2.5 | NO
M09AG2102 | HP SKIM SILO 1 AGITATOR | 2.5 | 2.5 | NO
M09AG2202 | HP SKIM SILO 2 AGITATOR | 2.5 | 2.5 | NO
C01PU4810 | CHEESE MILK PAST FEED PUMP | 2.5 | 2.5 | NO
C01PU4815 | CHEESE MILK PAST TIMING PUMP | 2.5 | 2.5 | NO
C01PU4880 | CHEESE MILK PAST HW PUMP | 2.5 | 2.5 | NO
M10PU2011 | LOADOUT SILOS TO LOAD OUT PUMP | 4 | 4 | NO
#REF! | LOADOUT SILOS TO PWDR1 STD PUMP | 2.5 | 2.5 | NO
M10PU2097 | LOADOUT SILOS CIPR PUMP | 2.5 | 2.5 | NO
M10AG2102 | LOADOUT SILO 1 AGITATOR | 2.5 | 2.5 | NO
M10AG2202 | LOADOUT SILO 2 AGITATOR | 2.5 | 2.5 | NO
A01PU2011 | ESL TKS TO FILLER 1 PUMP | 2.5 | 2.5 | NO
A01PU2012 | ESL TKS TO FILLER 2 PUMP | 2.5 | 2.5 | NO
A01PU2013 | ESL TKS TO ESL LOADOUT PUMP | 2.5 | 2.5 | NO
B01PU2031 | CRM CRYST TKS TO BUTTER PLANT PUMP | 2.5 | 2.5 | NO
A01PU2097 | CRM CRIST/ESL/DUAL TKS CIPR PUMP | 2.5 | 2.5 | NO
B01AG2102 | CRM CRIST TK 1 AGITATOR | 2.5 | 2.5 | NO
A01AG2102 | ESL TK 1 AGITATOR | 2.5 | 2.5 | NO
B01AG2202 | CRM CRIST TK 2 AGITATOR | 2.5 | 2.5 | NO
A01AG2202 | ESL TK 2 AGITATOR | 2.5 | 2.5 | NO
B01AG2402 | CRM CRYST TK 3 AGITATOR | 2.5 | 2.5 | NO
U01PU3410 | CIP SET 1 CIPS 1 PUMP | 10 | 10 | NO
U01PU3420 | CIP SET 1 CIPS 2 PUMP | 10 | 10 | NO
U01PU3513 | CIP SET 1 CAUSTIC TK RECIRC PUMP | 2.5 | 2.5 | NO
U01PU3613 | CIP SET 1 ACID TK RECIRC PUMP | 2.5 | 2.5 | NO
U06PU4340 | CONDENSATE RETURN PUMP | 2.5 | 2.5 | NO
B01MC0001 | BUTTER EGLI OEM | 70 | 70 | NO
A02MC0001 | ESL DS TRIPLE OEM | 70 | 70 | NO